Linecrew Bulletin

|  | [Click here to enter a date] |
| --- | --- |

# Overview

This bulletin will review the following:

- Two functions of the IFD Sensor

- IFD Shipping Lock

- Installing IFD equipped transformers

# Two functions of the IFD Sensor

Activated

Internal fault detection

- The IFD Sensor is a mechanical device that detects rapid pressure rises associated with low impedance faults

- When troubleshooting transformer outages, an activated IFD Sensor indicates that the transformer has faulted internally and must be replaced. No additional troubleshooting is required

## Pressure relief

- The IFD Sensor includes a PRV designed to automatically relieve tank pressures that develop from transformer load or ambient temperatures

- The PRV functions with or without the IFD Shipping Lock installed

Not Activated

IFD Shipping Lock

The IFD Shipping Lock prevents the IFD Sensor from activating while:

- Transporting the transformer

- Installing and preparing the transformer for field service

The Shipping Lock must remain installed until just prior to transformer energization.

IFD Shipping Lock

If an un-faulted transformer is removed from service, a Shipping Lock must be re-installed.

# Installing IFD equipped transformers

When installing IFD equipped transformers, the Shipping Lock must remain installed while:

- Moving or lifting the transformer

- Making cable connections

- Venting the PRV (if required)

- Changing or installing a bayonet fuse (if required)

Removing the Shipping Lock is the last step before transformer energization.

Installing IFD Equipped Pole-mounted Transformers

If the IFD Shipping Lock is removed early and the IFD Sensor activates prior to transformer energization, please contact Click or tap here to enter text. for support.

# Key points

- When troubleshooting a transformer outage, an activated IFD Sensor indicates that a field energized transformer has faulted internally and must be replaced. No further troubleshooting is required.

- When installing IFD equipped transformers, the Shipping Lock should only be removed immediately prior to transformer energization. It should be re-installed before moving an un-faulted transformer.

Installing IFD Equipped Pad-mounted Transformers

Do not re-energize or energize a transformer with an activated IFD Sensor. If the IFD Sensor activates prior to transformer energization, contact Click or tap here to enter text. for support.

# Resources

- An IFD Sensor Tailgate Training Video can be found at:

https://ifdtech.com/resources-for-utilities/

IFD Decal

Each transformer includes an IFD Decal which reviews the function of the IFD Sensor and the Shipping Lock